## Sheet1
Project Name | Project Description | Problem Summary
North Marysville substation 115kV loop-through | Convert the Transmission Line connection from the current Tap configuration to a Looped-in configuration. | North Marysville Substation is fed with a Tap connection to the transmission line which prevents the implementation of Auto-sectionalizing scheme to reduce the Customer Minutes Interruption that result from transmission faults.
Stimson Crossing to Sills Corner new transmission line | Design and construct approximately 5 miles of a new transmission line from Stimson Crossing Substation to Sills Corner. | North Stanwood and Camano Island load service area is supported via only one 115kV line, from Stimson Crossing – Stanwood – Camano. Loss of this line results in an outage to all the substations served by that line. A dedicated separate source from will reduce that exposure. This line will also help with operational flexibility and maintenance of the existing line from Stanwood to Camano. This project is required to complete the two independent transmission lines from Stimson Crossing switching station to serve Camano Island.
Stimson Crossing to North Stanwood transmssion line rebuild | Reconductor approximately 7 miles of the existing transmission line to larger conductor. | A portion of the Stimson Crossing - North Stanwood 115kV line has significant aging structures. Also, to increase the transmission network capacity and reliability in that area, the line segment needs to be reconductored with large wire.
Stimson Crossing substation upgrade | Convert the 115kV Stimson ring bus to a breaker-and-half configuration.
Jennings Park substation | Jennings Park substation will be built south of the existing Central Marysville substation as a replacement substation. Central Marysville subsation will be decomissioned and demolished. | The existing power transformer has been operated since 1984. Substation Construction & Maintenance Department recommends replacement because it is failure prone and safety concerns. Presently the substation is tapped and subject to large Customer Minutes of Interruption until personnel can be on site to perform manual switching following transmission line faults.
East Marysville Circuit Tie | Reconductor small wire to large conductor to provide a tie between two different East Marysville circuits to provide greater flexibilty and allow for feeding some of the expected load increse in the Whiskey Ridge area along 87th Ave. NE. | There are many localized subdivisions along 87th Ave. NE. These subdivisions are large and numerous. The development requires this circuit tie and wire conversion in order to adequately serve them. The reconductoring is appoximately 1400 ft along E Sunnyside School Rd at 87th Ave NE and approximately 580 ft along 87th Ave NE at E Sunnyside School Rd.
Getchell Switching Station | Design and construct a new 115kV transmission switching station at the northeast corner of Hwy 9 and 84th St NE. Four 115kV transmission lines with be built into the new switching station. Eventually one 115kV/12kV power transfomer bank will also be connected to the new switching station. | This project was identified in the Distric't 20-year, loag-range plan and is part of the North County transmission expansion plan to support load growth and transmission reliability. The North County service area reprsents approximately one-forth of the Disrtict's total load. Several large industrial customers have requested servie in the Marysville-Arlington area which increases the necessity of this project. This project helps minimize the impacts of outages on the transmission lines in the area. Defering this project will increase the risk of not being able to reliably serve the entire North County area.